DEPARTMENT OF ELECTRICAL AND ELECTRONICS ENGINEERING

# EE 2028   POWER QUALITY                                                       		                     3 0 0 100

- INTRODUCTION TO POWER QUALITY                                                                   3

Terms and definitions: Overloading, under voltage, sustained interruption; sags and swells; waveform distortion, Total Harmonic Distortion (THD), Computer Business Equipment Manufacturers Associations (CBEMA) curve.

2.	VOLTAGE SAGS AND INTERRUPTIONS                                                                  7

Sources of sags and interruptions, estimating voltage sag performance, motor starting sags, estimating the sag severity, mitigation of voltage sags, active series compensators, static transfer switches and fast transfer switches.

3.	OVERVOLTAGES                                                                                                          10

Sources of over voltages: Capacitor switching, lightning,  ferro resonance; mitigation of voltage swells: Surge arresters, low pass filters, power conditioners – Lightning protection, shielding, line arresters, protection of transformers and cables, computer analysis tools for transients, PSCAD and EMTP.

4.	HARMONICS                                                                                                                  12

Harmonic distortion: Voltage and current distortion, harmonic indices, harmonic sources from commercial and industrial loads, locating harmonic sources; power system response characteristics, resonance, harmonic distortion evaluation, devices for controlling harmonic distortion, passive filters, active filters, IEEE and IEC standards.

5.	POWER QUALITY MONITORING                                                                            13

Monitoring considerations: Power line disturbance analyzer, per quality measurement equipment, harmonic / spectrum analyzer, flicker meters, disturbance analyzer, applications of expert system for power quality monitoring.

L = 45   Total = 45

## REFERENCE BOOKS

- Roger.C.Dugan, Mark.F.McGranagham, Surya Santoso, H.Wayne Beaty, ‘Electrical Power Systems Quality’ McGraw Hill, 2003.

- PSCAD User Manual.

UNIT – 1: INTRODUCTION TO POWER QUALITY

TWO MARKS

- Define power quality .(Dec-12)

Power quality has been defined as the parameters of the voltage that affect the customers supersensitive equipment.

- What are the commonly used terms that describe the parameters of electrical power that describe or measure power quality.

Sag, swell, interruption, transients, harmonics, waveform distortion, over voltages, under voltages, voltage imbalance, power frequency variations, etc.

- What is the most common power quality problem.

Voltage sags are considered the most common power quality problem.. These can be caused by the utility or by customer loads. When sourced from the utility , they are most commonly caused by faults on the distribution system. These sags will be from 3 to 30 cycles and can be single or three phase. Depending on the design of the distribution system, a ground fault on 1 phase can cause a simultaneous swell on another phase.

- What is the second most common power quality problem?

Power quality problems are related to grounding, ground bonds and neutral to ground voltages, ground loops, ground current or ground associated issues.

- What type of equipment is affected by power quality issues?

All electrically operated or connected equipment is affected by power quality.

- What are the types of power quality solutions available on the market today?

There are hundreds  of manufacturers making thousands of different power quality solutions today. The categories of these solutions are :

- Utility based solutions for the substation level.

- User based solution for whole facility protection.

- User load level solutions for specific loads

- How can power quality problems be detected?

- A  piece of equipment misoperates at the same time of day.

- Circuit breakers trip without being overloaded.

- Equipment fails during a thunderstorm.

- Automated systems stop for no apparent reason.

- What are harmonics.(May-11)

Harmonics are distortions in the AC waveform. These distortions are caused by loads on the electrical system that use the electrical power at a different frequency than the fundamental 50 or 60 Hz.

- How do harmonics affect the electrical system.

In general harmonics cause magnetic portions of the electrical system to overheat. Such as transformers, line reactors, magnetic relays and power factor capacitors.

- How do harmonics affect the load.

The affect of harmonics on loads varies a great deal and is dependent on the load itself. Most loads are not affected by moderate levels of harmonics. Exceptions to this are loads that perform electrical measurements in the frequency domain of the harmonics.

- How do you measure power quality?

It requires power quality measurement equipment to measure , record and diagonos harmonic problems. Power quality instruments offer a service of characterizing all aspects of power quality and determining if it is acceptable to the load.

- Why is power conditioning needed?

Effective power conditioning will prevent the erosion of your equipment and by filtering out these harmful properties will substantially enhance its reliability.

- What types of equipment are affected by power line noise?

Any equipment based on semiconductor technology can be affected  which includes all computers , telecommunications PBXs and key systems, automated  manufacturing and design  systems, computerized medical equipment and point of sale terminals.

- Why are these transients or noise on the power line causing problems now?

Advances in digital logic technology have produced smaller and more sophisticated devices. This new generation of micro-circuitry is extremely dense and substantially more susceptible and transient damage.

- What represent quality of power?

This term covers technical aspects as well as non-technical aspects like the interaction between the customer and the network operator. Eg. The speed with which the network operator reacts to complaints, etc.

- What are the power quality issues?(Dec-13)

Power frequency disturbances, power system transients, grounding and bonding, electromagnetic interference , power system harmonics, electrostatic discharge, power factor.

- Classify power quality events in short duration events.

- Sag

- Swell

- Interruption.

- Mention the types of sag.

- Instantaneous sag.

- Momentary sag

- Temporary sag.

- Mention the types of swell .

- Instantaneous swell

- Momentary swell

- Temporary swell.

- List the types of interruption.(Dec-2009)

- Sustained interruption

- Momentary interruption

- Temporary interruption.

PART – B

- What are the major power quality issues and explain them.(Dec-13)/(Apr-14)

- Explain power quality and the reasons for increased concern in power quality. (Dec-13)/ (Apr-14)

- Explain the various types of power quality disturbances.(Dec-12)/(JUN-13)

- Explain the impacts of power quality.(Dec-2009)

- Discuss in detail about sags and swells.(Apr-14)

- Discuss in detail about transients.

- Define waveform distortion and explain the waveform distortion categories.

- Explain total harmonic distortion and total demand distortion.(Jun-11)

- Discuss the CBEMA curves and explain the events described in the curve.(Dec-13)/ (Jun-11)

- With a waveform sketch , explain the terms.

- Voltage sag.(Apr-14)/(JUN-13)

- Voltage interruption .(Apr-14)/(JUN-13)

- Voltage swells(JUN-13)

- Sag with harmonics.(JUN-13)

UNIT – 2: VOLTAGE SAGS AND INTERRUPTIONS

TWO MARKS

- What is voltage sag?(Dec-13)

A sag or dip is a decrease in RMS voltage or current at the power frequency for durations from 0.5 cycles to 1 minute, reported as the remaining voltage. Typical values are between 0.1 pu and 0.9 pu.

- When sag leads to interruption.

Voltage sag is a reduction in voltage for a short time. The voltage reduction magnitude is between 10 % to 90%  of  the normal root mean square (RMS) voltage at 50 Hz. An interruption is a complete loss of voltage or a drop to less than 10 % of nominal voltage in one or more phases.

- What are the causes of sag?(Apr-14)

- Voltage sags are usually associated with voltage sag.

- Equipment sensitive to both the magnitude and duration of voltage sag.

- Equipment sensitive to have characteristics other than magnitude and duration.

- What are the three levels of possible solutions to voltage sag and momentary interruption problems?

- Power System Design

- Equipment design

- Power conditioning equipment.

- List some industry standards associated with voltage sags.(Dec-13)

*SEMI F47-0200	8CBEMA curve

- What are the sources of sags and interruption?

- A sudden increase in load results in a corresponding sudden drop in voltage.

- Any sudden increase in load, if large enough will cause a voltage sag in motors, faults, switching.

- Recloser operation.

- Give some economic impacts due to sag.

- Process outrages

- Damaged products

- Lost time for restarting.

- What is the importance of estimating sag performance?

It is important to understand the expected voltage sag performance of the supply system so that facilities can be designed and equipment specifications developed to assure the optimum operation of production facilities.

- What are the various factors affecting the sag magnitude due to faults at a certain point in the system.

- Distance to the fault

- Fault impedance

- Type of fault

- Pre-sag voltage level

- System configuration

- System impedance

- Transformer connections.

- Name the different motor starting methods.

Resistance and reactance starters

Autotransformer starters

Star-Delta starters

- What are the causes for voltage sags due to transformer energizing?

- Normal system operation, which includes manual energizing of a transformer.

- Reclosing actions.

- How voltage sag can be mitigated.(Dec-13)

Voltage sag can be mitigated by voltage and power injections into the distribution system using power electronics based devices which are also known as custom power devices.

- Name the three levels of possible solutions to voltage sag and momentary interruption problems.

- Equipment Design	* Power conditioning equipment   Power system design

- Name any four types of sag mitigation devices.(Dec-13)

- Dynamic Voltage Restorer(DVR)       Active Series Compensators

- Distribution Static Compensator(DSTATCOM)

- Solid State Transfer Switches(SSTS)

- Define Dynamic Voltage Restorer (DVR).

A DVR is a solid state power electronics switching device consisting of either GTO or IGBT , a capacitor bank as an energy storage device and injection transformers. It is connected in series between a distributed system and a load.

- What is the important role of a DVR?

The basic idea of a DVR is to inject a controlled voltage generated generated by a forced commuted converter in series to the bus voltage by means of an injecting transformer.

- Define active series compensation devices.

A device that can boost the voltage by injecting a voltage in series with the remaining voltage during a voltage sag condition.

- What is the need of DSTATCOM?

It allows effective control of active and reactive power exchanges between the DSTATCOM  and the ac system.

- What is the main function of DSTATCOM?(Dec-13)

- Voltage regulation and compensation of reactive power

- Correction of power factor

- Elimination of current harmonics.

- What is the role of SSTS?(Dec-13)

- Can be used very effectively to protect sensitive loads against voltage sags, swells and other electrical disturbance.

- It ensures continuous high quality power supply to sensitive loads by transferring , within a time of milliseconds , the load from a faulted bus to a healthy one.

PART – B

- Discuss the sources of sags and interruption.

- Discuss in detail about the sag performance evaluation indices.

- Explain the sag performance evaluation methods.(JUN-13)

- Explain the various causes and effects of voltage sags.(JUN-13)

- What are the different voltage sag mitigation techniques? Explain in detail.

- Explain the principle of DVR operation used for sag mitigation.

- Discuss in detail about the active series compensator.

- Explain the solid state transfer switch with the transfer operation(Dec-13).

- Explain the system adapted to estimate the severity of the sag occurred due to various sources.

- Mention the standards associated with the voltage sag. (Dec-13)

UNIT – 3: OVERVOLTAGE TRANSIENTS

TWO MARKS

- Define transient over voltages. .(Dec-12)

A transient over voltage can be defined as the response of an electrical network to a sudden change in network conditions, either intended or accidental, (e.g. a switching operation or a fault) or network stimuli (e.g. lightning strike).

- What are the' types of transient overvoltages? .(Dec-13)

- Impulsive  		 2) Oscillatory

- Define impulsive transients. Give example for impulsive transient over voltages .(Dec-12)

An impulsive transient is a sudden, non-power frequency change in the steady state condition of the voltage and/or current waveforms that is essentially in one direction, either positive or negative, with respect to those waveforms.  The most common cause of this type of transient is lightning.

Give examples for oscillatory transient over voltages.

Switching operations within the distribution network are a major cause of oscillatory transient over    voltages. Such operations include

(a) Switching of utility capacitor banks,

(b) Switching of circuit breakers to clear network faults, and

(c) Switching of distribution feeders to rearrange the network for maintenance or construction

- What is the effect of capacitor switching transients on network?

Transients of this magnitude and duration are usually not a problem on the utility system, but they can produce problems at a user facility. Severe over voltages can appear on user facility capacitors through a phenomenon known as voltage magnification

- What are the causes of voltage magnification on network?

The voltage magnification will not result in capacitor damage. The problem that usually occurs is the failure or mis-operation of sensitive loads in the facility where the low voltage capacitors are installed.

- Define voltage magnification phenomena?

The highest transient voltages occur at the low voltage capacitor bank when the characteristic frequency of the switching transient is nearly equal to the resonant frequency of the low voltage system and when the switched capacitor is ten or more times the size of the low-voltage capacitor

- Mention the two important concerns for capacitor bank switching transients.

Voltage transients at the capacitor bank substation and neighboring substations

Power quality impact on sensitive customer loads due to variations in voltage when energizing capacitor banks

- Give the various aspects of equipment specific design and protection issues for the capacitor switching transients.

- Phase-to-ground and phase-to-phase insulation switching withstand to voltage stresses

- Controlled closing for circuit breakers (pre-insertion resistors/reactors or

synchronous switching)

- Capacitor bank and substation Circuit breakers ANSVIEEE C37 requirements ./ Current      limiting reactor requirements

- What specify the IEEE standard for shunt power capacitors causing transient overvoltages? (Dec-12)

The IEEE Standard for Shunt Power Capacitors, ANSI/IEEE Std. 18-1992, specifies that capacitors "may    reasonably be expected to withstand" transient overvoltages from 205% to 354% of rated peak voltage, depending on the number of times a year the overvoltage occurs.

- What are the various Causes of overvoltages? (Dec-13)

Overvoltages, can be attributed to the following main causes:

- Atmospheric discharges, i.e. lightning (LEMP - Lightning Electro-Magnetic Pulse)

- Switching operations in the public grid and low-voltage mains

- Electrostatic Discharges (ESD)             4.Ferroresonance

- Give tile basic principles of overvoltage protection of load equipments.

Limit the voltage across sensitive insulation.

Divert the surge current away from the load.

Block the surge current entering into the load.

Bonding of equipment with ground

- What is the need of surge arrestors? (Dec-13)

A surge arrester is a protective device for limiting surge voltages on equipment by discharging or bypassing surge current. Surge arresters allow only minimal flow of the 50Hz/60Hz power current to ground.

- Differentiate between transient voltage surge suppressors (TVSS) and surge arrestors.

Arresters and TVSS devices protect equipment from transient overvoltages by limiting the maximum voltage, and the terms are sometimes used interchangeably. However, TVSSs are generally associated with devices used at the load equipment. A TVSS will sometimes have more surge-limiting elements than an arrester.

- Mention the types of surge arrestors (Dec -13)

Metal-oxide varistor type          Gapped silicon - carbide type

- What is metal-oxide surge-arrester?

A metal-oxide surge-arrester (MOSA) utilizing zinc-oxide block provides the best performance, as surge voltage conduction starts and stops promptly at a precise voltage level, thereby improving system protection

- Give any two advantages of metal-oxide arresters over conventional silicon carbide distribution class arresters.

Improved Surge Duty Capability

Improved Temporary Overvoltage Capability

- What is the need of Transmission Line Arresters? 	'.

Transmission Line Surge Arresters conduct lightning surges around the protected insulator so that a lightning flashover is not created. They are designed to be installed functionally in parallel with the line insulator. The arrester conducts the lightning surges around the protected insulator so that a subsequent 50Hz / 60 Hz fault on the circuit is not created.

- Mention the Benefits of Transmission Line Surge Arresters

- Lowers initial cost of new or transmission line upgrades by making construction more compact and transmitting more energy in the same right of way.

- Reduces the height of transmission lines by eliminating shield wire

- Improves outage statistics by eliminating back flashover from the tower ground lead to the phase conductor

- What is the role of surge arrestor on shielded and unshielded transmission line?

On shielded transmission lines or under-built distribution circuits, the arrester prevents tower to phase insulator back-flashovers during a lightning strike.  On unshielded sub transmission or distribution circuits, the arrester prevents phase-to-ground flashover.

- What is the need of low pass filter in transient protection?

- This LC combination provides a low impedance path to ground for selected resonant frequencies.

- Low-pass filters employ pi principle to achieve better protection even for high- frequency transients.

- What is tire need of Shunt protectors or surge reduction filters?

  - An in-line filter specifically designed to reduce the rate of voltage rise (dv/dt) of the pre-clamped waveform.

  - It gives some series impedance between input and output terminals. This type of product is highly recommended for the protection of sensitive electronic equipment

- What is the application of Power Conditioners in transient protection?

Low-impedance power conditioners are used primarily to interface with the switch-mode power supplies found in electronic equipment. Low-impedance power conditioners differ from isolation transformers in that these conditioners have much lower impedance and have a filter as part of their design

- When on the device to position the power conditioners to avoid voltage swells.

- Differentiate between TVSS, Filter and Data/signal protection devices.

Transient: focus on limiting high-voltage spikes to an acceptable level.

Filtering: protect against low-energy transients and high frequency noise and finally Data/signal protection devices: Products that guard sensitive instrumentation against what we refer to as 'back door' transients and noise

25. Define lightning phenomena. (Apr-14)

Lightning is an electrical discharge in the air between clouds, between different charge centre within the same cloud, or between cloud and earth (or earthed object).

Even though more discharges occur between or within clouds, there are enough strokes that terminate on the earth to cause problems to power systems and sensitive electronic equipment

26. How Overvoltages are induced due to lightning?

- When lightning strikes occur in or near an electricity distribution system, lightning currents are generated and conducted through the power system into connected equipment.

- Large impulsive transient over voltages are produced as a result of this current flow.

27. What are the various causes due to lightning overvoltages?

- In transmission systems, the insulation is generally sufficient enough not to be endangered by induced voltages. However, distribution systems in which the insulation level is low, induced voltages are hazardous.

- When the induced voltage caused by lightning exceeds the strength of the insulation, a line flashover results, causing either temporary faults or disruption of services to customers

- What is the range of current induced due to lightning stroke?

The majority of the cloud to ground lightning strokes varies from kilo-Amperes to several tenths of kilo-amperes. Strokes above 100000 amperes are rare, and the highest reported peak value of the return stroke current is 200000 A. The shape of the current wave and the related voltage wave is rather capricious and different for every stroke.

- What is ferroresonance? (Dec-13)/ (Apr-14)

Ferro resonance is a special case of series LC resonance where the inductance involved is nonlinear and it is usually related to equipment with iron cores. It occurs when line capacitance resonates with the magnetizing reactance of a core while it goes in and out of saturation.

- Define ferroresonance phenomena. (Dec-13)

The phenomena of ferroresonance is a name given to a situation where the nonlinear magnetic properties of iron in transformer iron core interact with capacitance existing in the electrical network to produce a nonlinear tuned circuit with an unexpected resonant frequency. This phenomenon poses a hazard to an electric power system because it generates overvoltages and over currents.

- What are the problems associated with ferroresonance?

Transformer overheating

Audible noise

High overvoltages and surge arrester failure

32. What are the various capacitance produced by power system elements?

- The circuit-to-circuit capacitance

- Parallel lines capacitance

- Conductor to earth capacitance

- Circuit breaker grading capacitance

- Bus bar capacitance

- Bushing capacitance

33. List some common circumstances leading to ferroresonance problems.

Some common circumstances leading to ferroresonance include transformer fuse blowing, line or switch fuse blowing, energizing a new transformer by manual cable switching up-line from transformers, cable connector or splice opening, manual cable switching to reconfigure a cable circuit during emergency conditions, and open conductor fault in overhead line feeding cable.

34. Mention the common methods used for utility for protecting distribution transformer.

Generally utility to provide two common ways for protecting distribution transformer:

- Use transformers with interlaced secondary windings.

- Use surge arresters at low voltage terminals

35. Which are the most widely used protection devices in protection of transformer? Also  list the types mostly used.

Usually, in distribution transformers, MOV type surge arresters are used for overvoltage protection. 1.External Live Front arresters 2.Under Oil arresters 3.External Elbow arresters

36. Give the cable life equation as a function of impulses.

The cable life is an exponential function of the number of impulses of a certain magnitude that it receives, according 10 Hopkinton. The damage to the cable is related by

Dc = P . Ve
P = 	Number of impulses ;  V =  Magnitude of impulses

e =	 empirical constant ranging from 10 to 15

37. List the important types of arrestor used in protection of cable.(Dec-12)

(i) Under oil arresters (ii) Elbow arresters  (iii) Lower discharge arresters

38. What is the need of Computer analysis tools for transient studies? (Dec-13)

Computer analysis simulation tool can simulate the time response of the transient phenomena in the power system with a very high degree of accuracy.

39. List the advantages of computer analysis tools for transient studies. (Dec-13)

The application of commercial time-domain simulation packages (PSCAD/EMTDC) has many advantages over the conventional mathematical analytic methods, in terms of:

- There being no need to develop a complex nonlinear differential equation for the system;

- The complex power system phenomena such as ferroresonance, harmonics, etc being easily modeled with modules of lines, transformers, power converters, loads and protection equipment from the library.

40. What is the need of PSCAD/EMTDC? (Dec-13)

- EMTDC (Electromagnetic Transients including DC) represents and solves differential equations for both electromagnetic and electromechanical systems in the time domain.

- Solutions are calculated based on a fixed time step, and its program structure allows for the representation of control systems, either with or without electromagnetic or electromechanical systems present

41. Give any two analysis examples available in PSCAD/EMTDC? (Dec-13)

Transient Studies

- Transient over voltage studies (TOV)

- Line energizing (charging and discharging transients)

- Capacitor bank back to back switching, selection of inrush and out-rush reactors

Power Quality

- Voltage dips, swells and interruptions

- Induction motor starting

- System faults

- Voltage fluctuation

42. How to model a surge arrestor in PSCAD? (May-2008)

The frequency dependent model which was recommended by IEEE WG 3.4.11 (1992) is the most accurate representation based on single phase line model.

PART – B

- What are transient overvoltages? Explain the different types of transient overvoltages.

- Draw the CBEMA curve for transient overvoltages and explain (Dec-13)

- What are the different sources of transient overvoltages? Discuss the Capacitor switching transient.

- What are the important concerns for capacitor bank switching?

- Define lightning? Discuss in detail about the overvoltages due to lightning and the problems associated with it. (JUN-13)

- Explain in detail the mechanism of lightning (Apr-14).

- Draw the standardized waveform of the lightning induced voltage. Discuss about  the wave shape of the lightning current.

- Explain the phenomena of ferroresonance.(Dec-13)

- Explain the problems associated with ferroresonance. (Dec-13)

- What is the need for protection against overvoltages? What are the basic  principles of overvoltages protection of load equipments?

- Explain in detail about various methods to mitigate voltage swells

- Explain in detail about the surge arrestors and surge suppressors. (Dec-13)

- What are the advantages of surge arrestors? Discuss about the application module.

- Explain the following: (Dec-13)

- Low pass filters (b) Power conditioners (c) Surge filters

UNIT – 4   HARMONICS

TWO MARKS

- What are the important concepts to bear in mind to understand power system harmonics?

There are two important concepts to bear in mind with regard to power system harmonics. The first is the nature of harmonic current producing loads (nonlinear loads) and the second is the way in which harmonic currents flow and how the resulting harmonic voltages develop.

- Draw the relationship between between P, Q, S in sinusoidal condition.

- Define true power factor.

True power factor is calculated as the ratio between the total active power used in a circuit (including harmonics) and the total apparent power (including harmonics) supplied from the source

True power factor = Total active power (P) / apparent power (S)

- What is the reason for existence of harmonic distortion?

- Harmonics distortion exists due to the nonlinear characteristics of the devices and loads on the power system .

- These devices act as current sources that inject harmonic currents into the power system.

- Differentiate between linear loads and non-linear loads.

Linear load: Any load that draws current at supply fundamental frequency only is a linear load. The current drawn does not contain any harmonics (multiples of the supply frequency). Motors, resistors, inductors and capacitors are all linear loads.

Non Linear load: Any load that draws harmonic currents from the supply is a nonlinear load. The current waveform of such non-linear loads, is discontinuous and non sinusoidal because of the presence of harmonics.

- What is voltage and current distortion?

- Voltage distortion is any deviation from the nominal sine waveform of the AC line voltage .

- Current distortion is any deviation from the nominal sine waveform of the AC line current.

- Mention the commonly used indices used for measuring harmonic component of waveform.

The two most commonly used indices for measuring the ham10nic content of the waveform are the total harmonic distortion (THD) and total demand distortion (TDD).

1. If a generator produces a non-ideal sinusoidal waveform, the voltage waveform will contain a certain amount of harmonics

2. In motors, decreased efficiency, excessive heating, and vibration are symptoms of harmonic voltage distortion.

- Mention at least two causes of harmonics made on distribution systems.

In the distribution system, transformers are capable of producing harmonics due to magnetic core saturation. This is more prevalent at a lighter loading of the transformer

Large load currents in the neutral wires of a 3 phase system. Theoretically the neutral current can be up to the sum of all 3 phases therefore causing overheating of the neutral wires. Since only the phase wires are protected by circuit breakers of fuses, this can result in a potential fire hazard.

- What is harmonic index? State its significant.

The power quality industry has developed certain index values that help us assess the quality of service as it relates to distortion caused by the presence of harmonics. These values, or harmonic indices, serve as a useful metric of system performance. The two most commonly used indices under harmonic studies are

- Total harmonic distortion (TI-ID) (b) Total demand distortion (TDD)

- Mention the problems created by harmonics.

A large load current flows in the neutral WIres of a 3 phase system.

Theoretically the neutral current can be up to the sum of all 3 phases therefore causing overheating of the neutral wires. Poor power factor conditions that result in monthly utility penalty fees for major users (factories, manufacturing, and industrial) with a power factor less than 0.9.

- Mention the harmonic effects on devices and loads Insulation stress (voltage effect)

Thermal stress (current effect)

Load ruptures (abnormal operation)

- What is the effect on transformer due to Harmonics?

The primary effect of power system harmonics on transformers is the additional heat generated by the losses caused by the harmonic contents generated by the load current

- Mention he harmonic sources from commercial loads.

Single phase loads such as Switch mode power supplies, fluorescent lighting and UPS systems

Three phase loads such as high voltage AC drives system

- Mention the harmonic sources from industrial loads.

Three phase converter with Adjustable speed drives (DC drives and AC drives)

Arcing Devices (Arc furnaces, weiders, Discharge lamps etc)

Saturable devices (transformer, electromagnetic devices etc with steel core)

- What is the advantage of three phase converter?

Three-phase electronic power converters do not generate third-harmonic currents mainly when compared with single-phase converters. This is a great advantage because the third harmonic current is the largest component of harmonics shown in harmonics spectrum

- What is the disadvantage of 12 pulse drive?

The disadvantages of the l2-pulse drive are that there is more cost in control design and an extra transformer is usually required

- State the different types of inverters

Variable voltage inverter (VVI)

Current source inverter (CSI)

Pulse width modulated (PWM)

- What is Variable Voltage Inverter?

The variable voltage inverter (VVI), or square-wave six-step voltage source inverter (VSI), receives DC power from an adjustable voltage source (either from thyristor converter or DC-DC converter fed by Diode Bridge) and adjusts the frequency and voltage.

- What is current Source inverter?

The current source inverter (CSI) receives DC power from an adjustable current source and adjusts the frequency and current.

- What is the need of locating harmonic sources?

When harmonic problems are caused by excessive voltage distortion on the supply system, it is important to locate the sources of harmonics in order to develop a solution to the problem.

PART-B

- Explain briefly about fundamentals of harmonics generation and wave form distortion. (Dec-13)

- Explain in detail about classification of linear loads and non linear loads used in harmonic studies.

- Explain the concept of harmonic phenomena under the presence of harmonic producing loads.

- Explain for the following terms (i) Harmonic distortion (ii) Current distortion (iii) Voltage distortion (Dec-13)/(Jun-13)

- What are the two important harmonic indices ? Explain about it briefly. .(Dec-12)/(Jun-13)

- Give the power definitions under non sinusoidal conditions. Explain briefly about it.

- Differentiate between true power factor and displacement power factor under harmonic studies.

- Explain briefly about various harmonic characterization on power systems. (Jun-13)

- Explain briefly about the phenomena of how current distortion affects the voltage distortion under the presence of harmonics.

- What are the general causes of harmonics in power system?

- What are the various causes of harmonics in distribution power system? (Dec-13)/(jun-13)

- What are the effect of facility and site under the presence of harmonics?

- List the various effects of equipments due to harmonics. Explain briefly.

- Explain the harmonic effects on power system equipments briefly.

- What are the various classifications of harmonic sources and explain briefly about it?

- Explain IEEE and IEC standards on harmonics distortion (Jun-13)

UNIT – 5 	 POWER QUALITY MONITORING

TWO MARKS

- What is the importance of power quality monitoring?

Power Quality Monitoring is necessary to- detect and classify disturbance at a particular location on the power system.  PQ monitoring assists in preventive and predictive maintenance.  Problems can be detected before they cause widespread damage by sending automated alerts. PQ Monitoring can be used to determine the need for mitigation equipment.

- What are the monitoring objectives? (Dec-13)

- Continuous evaluation of the electric supply system for disturbances and power quality variations.

- Document performance of power conditioning equipment, such as static switches, UPS systems, other ride through technologies, and backup generators.

- What are the purposes of power quality monitoring system?(Apr-14)

- Preventive maintenance

- Load analysis

- Equipment diagnostics

- Long time surveys

- What is proactive monitoring? (Jun-13)

The traditional approach to power quality monitoring is reactive. We need to know when a problem is going to occur before it happens. Permanent power quality monitoring systems are designed to help proactively identify conditions and events that may cause problems should be addressed. This is called proactive monitoring.

- nd the response of equipment that may be sensitive to microsecond variations in the voltage.

- What are the steps involved in power quality monitoring? (Dec-13)

- Planning for the monitoring

- Preparing for the monitoring

- Inspecting the site

- Monitoring the power

- Analyzing, monitoring and inspecting data

- Applying corrective solutions

- What are the requirements of monitoring for a voltage regulation and unbalance?

- 3 phase voltages

- RMS magnitudes

- Continuous monitoring with periodic max/min/avg samples

- What are the requirements of monitoring for a harmonic distortion?

- Currents for response of equipment

- 3 phase voltages and currents

- Waveform characteristics

- 128 samples per cycle minimum

- Synchronized sampling of all voltages and currents

- Configurable sampling characteristics

- What are the Characteristics of power quality monitoring equipment?

Harmonic Analysis

Harmonic analyses are usually conducted by obtaining and interpreting measurements of waveforms. Equipment normally required to perform a harmonic study consists of a harmonic analyzer, an oscilloscope, and an RMS responding voltmeter and ammeter. Spectrum analysis is usually performed up to the 50th harmonic (3 kHz).

- What are the Characteristics of power line monitors?

- Portable, rugged, lightweight

- Simple to use, with proper training

- Designed for long-term unattended recording

- Definition of line disturbance parameters varies between manufacturers

- What is the Types of power quality measurement equipment?

- Hand-held single-phase power quality monitors

- Portable three-phase power quality monitors

- Harmonic analyzers

- Distortion analyzers

- Multimeters

- Mention the factors that should be considered  for selecting the instrument.

- Number of channels (voltage and/or current)

- Temperature specifications of the instrument

- Input voltage range (e.g., a to 1000 V)

- Ability to measure three-phase voltages

- What is the use of oscilloscope?

Oscilloscopes with fast sampling rates and automatic triggering function can be very useful for trace of transients.

- What is the use of spectrum analyzer?

A spectrum analyzer can be used for trace of high frequency harmonics.

- What is the use of simple single phase hand-held power quality monitor?

Power quality problems like measuring the occurrence of harmonics or checking the voltage level or the power frequency can easily be made by using a simple single phase hand-held power quality monitor.

- Mention the Instruments used for the analysis of non-sinusoidal voltage and currents?

- Oscilloscope

- Spectrum analyzer

- Harmonic analyzer

- Mention the basic categories of instruments for harmonic analysis?

- Simple meters

- General-purpose spectrum analyzers

- Special-purpose power system harmonic analyzers

- Digital Harmonics Measuring Equipment

- Distortion Analyzers

- Data Logger

- What is Spectrum analyzer?

An instrument used for the analysis and measurement of signals throughout the electromagnetic spectrum. Spectrum analyzers are available for sub audio, audio, and radio-frequency measurements, as well as for microwave and optical signal measurements.

- What is the operation of spectrum analyzer? (Dec-12)

A spectrum analyzer separates the signal into two components: amplitude (displayed vertically) and frequency (displayed horizontally). In some low frequency analyzers, phase information can also be displayed.

- Low-frequency analyzers are sometimes called as "Harmonic analyzers"

- Vertical scale displays the amplitude and horizontal scale displays the frequency.

- What is Swept heterodyne technique?

Any signal at the input, at a frequency such that the difference between its frequency and the local oscillator is within the bandwidth of an intermediate- frequency filter, will be detected and will vertically deflect the spot on the display by an amount proportional to the amplitude of the input signal being analyzed.

- What is FFT (or) digital technique used for harmonic analysis?

The signal to be analyzed is converted to a digital signal by using an analog to digital converter, and the digital signal is processed by using the FFT algorithm.  The algorithm analyzes the time domain waveform, computes the frequency components present, and displays the results.

- What are the advantages of FFT?

- FFT technique is much faster.

- Measurement is virtually real time.

- What are the disadvantages of FFT?

- Restricted to lower frequencies.

- Complex due to need of A/D converter.

- What is the use of digital storage?

Digital storage gives the effect of a constant display, even though a very slow sweep may have been used to acquire the displayed data.

- What is tracking generator?

The tracking generator enhances the applications of spectrum analyzers. Its output delivers a swept signal whose instantaneous frequency is always equal to the input tuned frequency of the analyzer.

- What is harmonic analyzer?

Spectrum analyzers covering up to typically 100 kHz can also be called harmonic analyzers.

Part-B

- Bring out the significance of power quality monitoring. What are the important

power quality monitoring objectives?

- Explain proactive monitoring.

- Discuss in detail about the selection of power quality monitoring sites.

- Explain the steps involved in power quality monitoring. What are the information from monitoring site surveys?

- Bring out the important characteristics of power quality variation.

- Write short notes on power quality measurement system. What are the characteristic of power quality measurement equipments?

- Write notes on power line disturbance analyzer.

8. 	What are the various instruments used for power quality measurements? What are the factors to be considered when selecting the instruments?

- Discuss in detail about the instruments used for analyzing non sinusoidal voltage and currents.

- Explain Harmonic/Spectrum analyzer. (Dec-13)

- Define voltage flicker. Discuss some of the flicker sources. Write notes on common methods for mitigation of flicker.

- Discuss in detail about the flicker meter. (Dec-13)

- Explain the modem power quality monitors.

- Bring out the applications of expert system for power quality monitoring. (May-11)

- Draw and explain the functional structure of expert systems.

- Draw the block diagram of advanced power quality monitoring systems. Explain it. (Dec-13)/(jun-13)